## How to use
DCS FORM 2 — PID, MAN, SUMA faceplate parameters
Open the faceplate of each tag in the DCS. MNO = module number (MNO 14 = S1-MDL014); station 101 = S1.
Write the value exactly as the faceplate shows it, in the unit of the row 2 header. "=" means the same as the column before. Put an x in OK when the row is done.
The rows are sorted by station and MNO (the filter buttons let you sort in another way). Sheets: PID (incl. PIDV), MAN, SUMA, Sim now (reference: what the simulator uses at the moment).
The meaning of each column is the assistant's reading of the faceplate names: tell me if one is wrong.
Type | Column | Faceplate name — meaning | Unit | Used by the simulator now?
PID | PH | PV high (range / alarm limit: write what it shows) | PV unit | yes
PID | PL | PV low (range / alarm limit: write what it shows) | PV unit | yes
PID | SH | SV limit high | PV unit | not yet (recorded to be used)
PID | SL | SV limit low | PV unit | not yet (recorded to be used)
PID | MH | MV limit high | % | yes
PID | ML | MV limit low | % | yes
PID | dMVH | MV rate limit | % | not yet (recorded to be used)
PID | P | Proportional band (gain = 100 / P) | % | yes
PID | I | Integral time | sec | yes
PID | D | Derivative time | sec | yes
PID | DTI | Calculation interval | sec | not yet (recorded to be used)
PID | TF | Input filter time | sec | not yet (recorded to be used)
PID | GAP | Gap (no action inside) | % | not yet (recorded to be used)
PID | BND | Output band | % | not yet (recorded to be used)
PID | CUT | Low cut-off | % | not yet (recorded to be used)
PID | DH | Deviation limit (alarm) | % | not yet (recorded to be used)
PID | PHONDT | PV high on-delay time | sec | not yet (recorded to be used)
PID | PLONDT | PV low on-delay time | sec | not yet (recorded to be used)
MAN | PH | PV high (range / alarm limit: write what it shows) | PV unit | yes
MAN | PL | PV low (range / alarm limit: write what it shows) | PV unit | yes
MAN | SH | SV limit high | PV unit | not yet (recorded to be used)
MAN | SL | SV limit low | PV unit | not yet (recorded to be used)
MAN | MH | MV limit high | % | yes
MAN | ML | MV limit low | % | yes
MAN | DH | Deviation limit (alarm) | % | not yet (recorded to be used)
MAN | DT | Calculation interval | sec | not yet (recorded to be used)
MAN | TF | Input filter time | sec | not yet (recorded to be used)
MAN | FSC | Full stroke time | min | not yet (recorded to be used)
MAN | CUT | Low cut-off | % | not yet (recorded to be used)
MAN | PHONDT | PV high on-delay time | sec | not yet (recorded to be used)
MAN | PLONDT | PV low on-delay time | sec | not yet (recorded to be used)
SUMA | PH | PV high (limit: write what it shows) | PV unit | not yet (recorded to be used)
SUMA | PL | PV low (limit: write what it shows) | PV unit | not yet (recorded to be used)
SUMA | RSTS | Reset / limit value of the total | total unit | not yet (recorded to be used)
SUMA | K | K (scale factor of the total) | - | not yet (recorded to be used)
SUMA | DT | Calculation interval | sec | not yet (recorded to be used)
SUMA | TF | Input filter time | sec | not yet (recorded to be used)
SUMA | CUT | Low cut-off | % | not yet (recorded to be used)
SUMA | PHONDT | PV high on-delay time | sec | not yet (recorded to be used)
SUMA | PLONDT | PV low on-delay time | sec | not yet (recorded to be used)
SUMA | SUM unit | Unit of the total (T, kg, m3 ...) | text | not yet (recorded to be used)

## PID
PID — sorted by station and MNO. Write the faceplate values in the white columns.
# | Station | Sheet | Tag | MNO | Description | PV address / IO tag | PV unit | PH | PL | SH | SL | MH | ML | dMVH | P | I | D | DTI | TF | GAP | BND | CUT | DH | PHONDT | PLONDT | OK | Notes
[8 empty] | unit | unit | unit | unit | % | % | % | % | sec | sec | sec | sec | % | % | % | % | sec | sec
1 | 101 | ABC-001C | PIC-COBM | 6 | #1 Boiler finishing superheater outlet main steam pressure | AI0131 [PT-MS1002] | Kg/cm2
2 | 101 | ABC-012 | TICMS1004 | 9 | #1 Boiler finishing S/H outlet main steam temp. (1) | AI0612 [TT-MS1004-1] ¦ AI0644 [TT-MS1004-2] | °C
3 | 101 | ABC-002 | AICFG112 | 10 | COMBUSTION AIR CONTROL |  | %
4 | 101 | ABC-004A | FIC-CF | 14 | #1 Coal feeder-A feedrate | AI0480 [MIF-CL1061-A] | %
5 | 101 | ABC-004A | FIC-CM | 15 | #1 Coal feeder-A feedrate | AI0480 [MIF-CL1061-A] | T/H
6 | 101 | ABC-011 | TICBR1130 | 16 | #1 Superheater NO.2 inlet header steam temperature (1) | AI0609 [TT-BR1130-1] ¦ AI0641 [TT-BR1130-2] | °C
7 | 101 | ABC-011 | TICBR1140 | 17 | #1 Superheater NO.2 outlet header steam temperature (1) | AI0610 [TT-BR1140-1] ¦ AI0642 [TT-BR1140-2] | °C
8 | 101 | ABC-012 | TICBR1150 | 18 | #1 Finishing S/H inlet header steam temperature (1) | AI0611 [TT-BR1150-1] ¦ AI0643 [TT-BR1150-2] | °C
9 | 101 | ABC-029 | PICDO1008 | 19 | #1 Boiler start up burner diesel oil circulation line oil pressure | AI0514 [PT-DO1008] | kg/cm2
10 | 101 | ABC-010 | LICBR1001 | 20 | #1 Boiler drum level (1) | AI0130 [LT-BR1001-1] ¦ AI0128 [PT-BR1001-1] | mm
11 | 101 | ABC-010 | LICBR1001A | 21 | #1 Boiler drum level (1) | AI0130 [LT-BR1001-1] ¦ AI0128 [PT-BR1001-1] | mm
12 | 101 | ABC-010 | FICFW1007 | 22 | DRUM LEVEL CONTROL (FEED WATER FLOW CONTROL) |  | T/H
13 | 101 | ABC-007 | FICFA1071 | 23 | PAF/SAF AIR FLOW CONTROL |  | T/H
14 | 101 | ABC-007 | FICFA1081 | 24 | PAF/SAF AIR FLOW CONTROL |  | T/H
15 | 101 | ABC-014 | FICFA1055A | 25 | FLUIDIZING AIR FLOW CONTROL |  | T/H
16 | 101 | ABC-014 | FICFA1055B | 26 | FLUIDIZING AIR FLOW CONTROL |  | T/H
17 | 101 | ABC-003A | FICFA1043A | 27 | #1 Boiler start up burner-A hot secondary air inlet flow | AI0164 [FT-FA1043-A] ¦ AI0515 [FT-DO1043-A] | T/H
18 | 101 | ABC-003B | FICFA1043B | 28 | #1 Boiler start up burner-B hot secondary air inlet flow | AI0290 [FT-FA1043-B] ¦ AI0546 [FT-DO1043-B] | T/H
19 | 101 | ABC-008 | PICFG108A | 29 | FURNACE PRESSURE CONTROL |  | mmH2O
20 | 101 | ABC-013 | PICMS1002 | 30 | MAIN STEAM PRESSURE CONTROL (BLOW-OFF) |  | kg/cm2
21 | 101 | ABC-009A | DPICFG108 | 31 | #1 Furnace plenum/upper layer diff. pressure (A) | AI0134 [DPT-FG1081] ¦ AI0262 [DPT-FG1082] | mmH2O
22 | 101 | ABC-009A | PIC-BASC | 32 | #1 Furnace plenum/upper layer diff. pressure (A) | AI0134 [DPT-FG1081] ¦ AI0262 [DPT-FG1082] | %
23 | 101 | ABC-003A | FICDO1043A | 33 | #1 Boiler start up burner-A supply line oil flow | AI0515 [FT-DO1043-A] | T/H
24 | 101 | ABC-003B | FICDO1043B | 34 | #1 Boiler start up burner-B supply line oil flow | AI0546 [FT-DO1043-B] | T/H
25 | 101 | ABC-003C | FICDO1043C | 35 | #1 Boiler start up burner-C supply line oil flow | AI0517 [FT-DO1043-C] | T/H
26 | 101 | ABC-008 | PICFG108 | 36 | FURNACE PRESSURE CONTROL |  | mmH2O
27 | 101 | ABC-005 | AICFG10571 | 37 | #1 Stack outlet flue gas SOx value | AI0466 [AT-FG1057-1] | ppm
28 | 101 | ABC-003D | FICDO1043D | 38 | #1 Boiler start up burner-D supply line oil flow | AI0548 [FT-DO1043-D] | T/H
29 | 101 | ABC-054 | PICHR1391 | 46 | #1 Hot reheat steam blow-off motor valve position | AI0737 [ZT-HR1391] | kg/cm2
30 | 101 | ABC-010 | LICBR1001B | 49 | #1 Boiler drum level (1) | AI0130 [LT-BR1001-1] ¦ AI0128 [PT-BR1001-1] | mm
31 | 101 | ABC-004A | HS-COAL | 51 | COAL MASTER CONTROL & A-COAL FEEDER CONTROL
32 | 101 | ABC-003A | PICDO1043A | 62 | #1 Boiler start up burner-A diesel oil supply line oil pressure | AI0293 [PT-DO1043-A2] | kg/cm2
33 | 101 | ABC-003B | PICDO1043B | 63 | #1 Boiler start up burner-B diesel oil supply line oil pressure | AI0439 [PT-DO1043-B2] | kg/cm2
34 | 101 | ABC-003C | PICDO1043C | 64 | #1 Boiler start up burner-C diesel oil supply line oil pressure | AI0596 [PT-DO1043-C2] | kg/cm2
35 | 101 | ABC-003D | PICDO1043D | 65 | #1 Boiler start up burner-D diesel oil supply line oil pressure | AI0771 [PT-DO1043-D2] | kg/cm2
36 | 101 | ABC-055 | HICBR1391 | 71 | #1 S/H NO.1 outlet header to reheater motor valve position | AI0181 [ZT-BR1391] | %
37 | 101 | ABC-003E | FIC-OM | 164 | OIL MASTER CONTROL
38 | 101 | ABC-003C | FICFA1043C | 197 | #1 Boiler start up burner-C hot secondary air inlet flow | AI0403 [FT-FA1043-C] ¦ AI0517 [FT-DO1043-C] | T/H
39 | 101 | ABC-003D | FICFA1043D | 198 | #1 Boiler start up burner-D hot secondary air inlet flow | AI0597 [FT-FA1043-D] ¦ AI0548 [FT-DO1043-D] | T/H
40 | 102 | ABC-017 | PICSB1052 | 1 | #1 Boiler sootblower header steam pressure | AI0533 [PT-SB1052] | kg/cm2
41 | 102 | ABC-050 | PICMS1006 | 2 | #1 Turbine main steam pressure(1) | AI0416 [PT-MS1006-1] ¦ AI0512 [PT-MS1006-2] | kg/cm2
42 | 102 | ABC-051 | TICMS1022 | 3 | #1 HP turbine bypass outlet temperature (1) | AI0865 [TT-MS1022-1] ¦ AI0897 [TT-MS1022-2] | °C
43 | 102 | ABC-031 | LICCD1104 | 4 | COND. DUMPING TO RAW PIT / COND. MAKE-UP WATER / DEAERATOR LEVEL CONTROL |  | mm
44 | 102 | ABC-019 | TICHR1002 | 5 | #1 Reheater outlet header temperature (1) | AI0867 [TT-HR1002-1] ¦ AI0899 [TT-HR1002-2] | °C
45 | 102 | ABC-020 | TICHR1002A | 6 | REHEATER/SUPERHEATER FLUE GAS DAMPER CONTROL |  | °C
46 | 102 | ABC-030 | PICAS1004 | 7 | #1 Main steam pipe to aux. steam supply pressure | AI0514 [PT-AS1004] ¦ AI0515 [PT-AS1005] | kg/cm2
47 | 102 | ABC-030 | PICAS1005 | 8 | #1 Cold reheat to aux. steam supply pressure | AI0515 [PT-AS1005] ¦ AI0514 [PT-AS1004] | kg/cm2
48 | 102 | ABC-056 | PICCD1104 | 9 | #1 Boiler deaerator pressure | AI0417 [PT-CD1104] | kg/cm2
49 | 102 | ABC-031 | LICCD1110A | 10 | #1 Condenser hot well water level | AI0640 [LT-CD1110] | mm
50 | 102 | ABC-031 | LICCD1110B | 11 | #1 Condenser hot well water level | AI0640 [LT-CD1110] | mm
51 | 102 | ABC-032 | FICCD1120 | 12 | #1 Condensate water flow | AI0437 [FT-CD1120] | T/H
52 | 102 | ABC-032 | FICCD1121 | 13 | #1 Condensate polisher inlet water flow | AI0436 [FT-CD1121] ¦ AI0437 [FT-CD1120] | T/H
53 | 102 | ABC-033 | TICAS1001 | 14 | #1 Main steam to aux. steam desuperheater temperature | AI0641 [TT-AS1001] | °C
54 | 102 | ABC-034 | TICAS1017 | 15 | #1 Gland steam turbine side temperature | AI0902 [TT-AS1017] | °C
55 | 102 | ABC-035 | LICHD11051 | 16 | #1 NO.1 HPH level (1) | AI0676 [LT-HD1105-1] ¦ AI0852 [LT-HD1105-2] | mm
56 | 102 | ABC-035 | LICHD11052 | 17 | #1 NO.1 HPH level (2) | AI0852 [LT-HD1105-2] ¦ AI0676 [LT-HD1105-1] | mm
57 | 102 | ABC-036 | LICHD11061 | 18 | #1 NO.2 HPH level (1) | AI0677 [LT-HD1106-1] ¦ AI0853 [LT-HD1106-2] | mm
58 | 102 | ABC-036 | LICHD11062 | 19 | #1 NO.2 HPH level (2) | AI0853 [LT-HD1106-2] ¦ AI0677 [LT-HD1106-1] | mm
59 | 102 | ABC-037 | LICHD11011 | 20 | #1 NO.1 LPH level (1) | AI0673 [LT-HD1101-1] ¦ AI0849 [LT-HD1101-2] | mm
60 | 102 | ABC-037 | LICHD11012 | 21 | #1 NO.1 LPH level (2) | AI0849 [LT-HD1101-2] ¦ AI0673 [LT-HD1101-1] | mm
61 | 102 | ABC-038 | LICHD11021 | 22 | #1 NO.2 LPH level (1) | AI0674 [LT-HD1102-1] ¦ AI0850 [LT-HD1102-2] | mm
62 | 102 | ABC-038 | LICHD11022 | 23 | #1 NO.2 LPH level (2) | AI0850 [LT-HD1102-2] ¦ AI0674 [LT-HD1102-1] | mm
63 | 102 | ABC-039 | LICHD11031 | 24 | #1 NO.3 LPH level (1) | AI0675 [LT-HD1103-1] ¦ AI0851 [LT-HD1103-2] | mm
64 | 102 | ABC-039 | LICHD11032 | 25 | #1 NO.3 LPH level (2) | AI0851 [LT-HD1103-2] ¦ AI0675 [LT-HD1103-1] | mm
65 | 102 | ABC-052 | PICHR1003 | 26 | #1 HP turbine first stage steam pressure (A) | AI0883 [PT-ST1001-1] ¦ AI0884 [PT-ST1001-2] | kg/cm2
66 | 102 | ABC-052 | TICHR1012 | 27 | #1 LP turbine bypass outlet temperature (1) | AI0864 [TT-HR1012-1] ¦ AI0896 [TT-HR1012-2] | °C
67 | 102 | ABC-053 | TICLO1002 | 28 | #1 Turbine rated speed | AI0534 [TCS-AI1004] ¦ AI0452 [TE-LO1002-1] | °C
68 | 105 | ABC-028 | PICDO0005 | 1 | Diesel oil pump outlet to start-up burner oil pressure | AI0181 [PT-DO0005] | kg/cm2

## MAN
MAN — sorted by station and MNO. Write the faceplate values in the white columns.
# | Station | Sheet | Tag | MNO | Description | PV address / IO tag | PV unit | PH | PL | SH | SL | MH | ML | DH | DT | TF | FSC | CUT | PHONDT | PLONDT | OK | Notes
[8 empty] | unit | unit | unit | unit | % | % | % | sec | sec | min | % | sec | sec
1 | 101 | ABC-001A | HIC-ULD | 2 | COORDINATED CONTROL SYSTEM |  | MW
2 | 101 | ABC-001A | HIC-MWHL | 3 | COORDINATED CONTROL SYSTEM |  | MW
3 | 101 | ABC-001A | HIC-MWLL | 4 | COORDINATED CONTROL SYSTEM |  | MW
4 | 101 | ABC-001B | HIC-MWRL | 5 | COORDINATED CONTROL SYSTEM |  | MW/MIN
5 | 101 | ABC-001C | HIC-BM | 7 | #1 Boiler finishing superheater outlet main steam pressure | AI0131 [PT-MS1002] | %
6 | 101 | ABC-001C | EIC-TM | 8 | #1 Boiler finishing superheater outlet main steam pressure | AI0131 [PT-MS1002] | MW
7 | 101 | ABC-004A | FICCL1061A | 11 | #1 Coal feeder-A feedrate | AI0480 [MIF-CL1061-A] | T/H
8 | 101 | ABC-004B | FICCL1061B | 12 | #1 Coal feeder-B feedrate | AI0512 [MIF-CL1061-B] | T/H
9 | 101 | ABC-004C | FICCL1061C | 13 | #1 Coal feeder-C feedrate | AI0544 [MIF-CL1061-C] | T/H
10 | 101 | ABC-009A | HICL1060A | 39 | FURNACE DIFF. PRESSURE CONTROL (A/B/C-BOTTOM ASH SCREW COOLER) |  | rpm
11 | 101 | ABC-009A | HICL1060B | 40 | FURNACE DIFF. PRESSURE CONTROL (A/B/C-BOTTOM ASH SCREW COOLER) |  | rpm
12 | 101 | ABC-009A | HICL1060C | 41 | FURNACE DIFF. PRESSURE CONTROL (A/B/C-BOTTOM ASH SCREW COOLER) |  | rpm
13 | 101 | ABC-009B | HICL1060D | 42 | D-BOTTOM ASH SCREW COOLER CONTROL |  | rpm
14 | 101 | ABC-002 | HS-OIL | 43 | COMBUSTION AIR CONTROL |  | Kcal / Kg
15 | 101 | ABC-003A | HIC-AFAR | 44 | A-START UP BURNER CONTROL (FUEL / AIR)
16 | 101 | ABC-003B | HIC-BFAR | 45 | B-START UP BURNER CONTROL (FUEL / AIR)
17 | 101 | ABC-002 | HS-O2 | 48 | COMBUSTION AIR CONTROL |  | %
18 | 101 | ABC-002 | HIC-TADBS | 50 | COMBUSTION AIR CONTROL |  | T/H
19 | 101 | ABC-004A | A-BIAS | 52 | COAL MASTER CONTROL & A-COAL FEEDER CONTROL |  | T/H
20 | 101 | ABC-004B | B-BIAS | 53 | B-COAL FEEDER CONTROL |  | T/H
21 | 101 | ABC-004C | C-BIAS | 54 | C-COAL FEEDER CONTROL |  | T/H
22 | 101 | ABC-009A | SICL1060A | 55 | #1 Bottom ash cooler-A converter speed | AI0150 [ST-L1060A] | rpm
23 | 101 | ABC-009A | SICL1060B | 56 | #1 Bottom ash cooler-B converter speed | AI0279 [ST-L1060B] | rpm
24 | 101 | ABC-009A | SICL1060C | 57 | #1 Bottom ash cooler-C converter speed | AI0407 [ST-L1060C] | rpm
25 | 101 | ABC-009B | SICL1060D | 58 | #1 Bottom ash cooler-D converter speed | AI0769 [ST-L1060D] | rpm
26 | 101 | ABC-003C | HIC-CFAR | 59 | C-START UP BURNER CONTROL (FUEL / AIR)
27 | 101 | ABC-003D | HIC-DFAR | 60 | D-START UP BURNER CONTROL (FUEL / AIR)
28 | 101 | ABC-029 | HICDO1012 | 61 | #1 Diesel oil pump to burner pressure control valve position | AI0276 [ZT-DO1012] | %
29 | 101 | ABC-003A | HIC-SADBSA | 158 | A-START UP BURNER CONTROL (FUEL / AIR) |  | T/H
30 | 101 | ABC-003B | HIC-SADBSB | 159 | B-START UP BURNER CONTROL (FUEL / AIR) |  | T/H
31 | 101 | ABC-003C | HIC-SADBSC | 160 | C-START UP BURNER CONTROL (FUEL / AIR) |  | T/H
32 | 101 | ABC-003D | HIC-SADBSD | 161 | D-START UP BURNER CONTROL (FUEL / AIR) |  | T/H
33 | 102 | ABC-020 | HICHR1002A | 31 | REHEATER/SUPERHEATER FLUE GAS DAMPER CONTROL |  | %
34 | 102 | ABC-020 | HICHR1002B | 32 | REHEATER/SUPERHEATER FLUE GAS DAMPER CONTROL |  | %
35 | 103 | ABC-015 | HICFA1005 | 1 | #1 Furnace temp. front wall motor control damper FA1005 position | AI0544 [ZT-FA1005] | %
36 | 103 | ABC-015 | HICFA1006 | 2 | #1 Furnace temp. front wall motor control damper FA1006 position | AI0545 [ZT-FA1006] | %
37 | 103 | ABC-015 | HICFA1007 | 3 | #1 Furnace temp. front wall motor control damper FA1007 position | AI0546 [ZT-FA1007] | %
38 | 103 | ABC-015 | HICFA1008 | 4 | #1 Furnace temp. front wall motor control damper FA1008 position | AI0547 [ZT-FA1008] | %
39 | 103 | ABC-015 | HICFA1009 | 5 | #1 Furnace temp. front wall motor control damper FA1009 position | AI0548 [ZT-FA1009] | %
40 | 103 | ABC-015 | HICFA1010 | 6 | #1 Furnace temp. front wall motor control damper FA1010 position | AI0549 [ZT-FA1010] | %
41 | 103 | ABC-015 | HICFA1011 | 7 | #1 Furnace temp. front wall motor control damper FA1011 position | AI0550 [ZT-FA1011] | %
42 | 103 | ABC-015 | HICFA1012 | 8 | #1 Furnace temp. front wall motor control damper FA1012 position | AI0560 [ZT-FA1012] | %
43 | 103 | ABC-015 | HICFA1013 | 9 | #1 Furnace temp. front wall motor control damper FA1013 position | AI0561 [ZT-FA1013] | %
44 | 103 | ABC-015 | HICFA1014 | 10 | #1 Furnace temp. front wall motor control damper FA1014 position | AI0562 [ZT-FA1014] | %
45 | 103 | ABC-015 | HICFA1015 | 11 | #1 Furnace temp. front wall motor control damper FA1015 position | AI0563 [ZT-FA1015] | %
46 | 103 | ABC-015 | HICFA1016 | 12 | #1 Furnace temp. front wall motor control damper FA1016 position | AI0564 [ZT-FA1016] | %
47 | 103 | ABC-016 | HICFA1017 | 13 | #1 Furnace temp. front wall motor control damper FA1017 position | AI0565 [ZT-FA1017] | %
48 | 103 | ABC-016 | HICFA1018 | 14 | #1 Furnace temp. front wall motor control damper FA1018 position | AI0566 [ZT-FA1018] | %
49 | 103 | ABC-016 | HICFA1019 | 15 | #1 Furnace temp. rear wall motor control damper FA1019 position | AI0416 [ZT-FA1019] | %
50 | 103 | ABC-016 | HICFA1020 | 16 | #1 Furnace temp. rear wall motor control damper FA1020 position | AI0417 [ZT-FA1020] | %
51 | 103 | ABC-016 | HICFA1021 | 17 | #1 Furnace temp. rear wall motor control damper FA1021 position | AI0418 [ZT-FA1021] | %
52 | 103 | ABC-016 | HICFA1022 | 18 | #1 Furnace temp. rear wall motor control damper FA1022 position | AI0419 [ZT-FA1022] | %
53 | 103 | ABC-016 | HICFA1023 | 19 | #1 Furnace temp. rear wall motor control damper FA1023 position | AI0420 [ZT-FA1023] | %
54 | 103 | ABC-016 | HICFA1024 | 20 | #1 Furnace temp. rear wall motor control damper FA1024 position | AI0421 [ZT-FA1024] | %
55 | 103 | ABC-016 | HICFA1025 | 21 | #1 Furnace temp. rear wall motor control damper FA1025 position | AI0422 [ZT-FA1025] | %
56 | 103 | ABC-016 | HICFA1026 | 22 | #1 Furnace temp. rear wall motor control damper FA1026 position | AI0423 [ZT-FA1026] | %
57 | 103 | ABC-057 | HICFABIASU | 23 | FURNACE TEMPERATURE (3) |  | %
58 | 103 | ABC-057 | HICFABIASL | 24 | FURNACE TEMPERATURE (3) |  | %

## SUMA
SUMA — sorted by station and MNO. Write the faceplate values in the white columns.
# | Station | Sheet | Tag | MNO | Description | PV address / IO tag | PV unit | PH | PL | RSTS | K | DT | TF | CUT | PHONDT | PLONDT | SUM unit | OK | Notes
[8 empty] | unit | unit | total unit | - | sec | sec | % | sec | sec | text
1 | 101 | ABC-003A | FIQDO1043A | 173 | #1 Boiler start up burner-A supply line oil flow | AI0515 [FT-DO1043-A] | T/H
2 | 101 | ABC-003B | FIQDO1043B | 174 | #1 Boiler start up burner-B supply line oil flow | AI0546 [FT-DO1043-B] | T/H
3 | 101 | ABC-003C | FIQDO1043C | 175 | #1 Boiler start up burner-C supply line oil flow | AI0517 [FT-DO1043-C] | T/H
4 | 101 | ABC-003D | FIQDO1043D | 176 | #1 Boiler start up burner-D supply line oil flow | AI0548 [FT-DO1043-D] | T/H
5 | 101 | ABC-010 | FIQFW10071 | 181 | #1 Boiler feed water flow (1) | AI0256 [FT-FW1007-1] ¦ AI0592 [TT-FW1160] | T/H
6 | 101 | ABC-010 | FIQFW10072 | 182 | #1 Boiler feed water flow (2) | AI0384 [FT-FW1007-2] ¦ AI0592 [TT-FW1160] | T/H
7 | 101 | ABC-001C | FIQMS1031 | 184 | #1 Boiler main steam flow | AI0129 [FT-MS1031] ¦ AI0131 [PT-MS1002] | T/H
8 | 101 | ABC-005 | LIME-SUM | 196 | #1 Limestone feeder speed | AI0151 [ST-M1311] | %
9 | 102 | ABC-032 | FIQCD1121 | 86 | #1 Condensate polisher inlet water flow | AI0436 [FT-CD1121] | T/H
10 | 102 | ABC-032 | FIQCD1120 | 87 | #1 Condensate water flow | AI0437 [FT-CD1120] | T/H

## Sim now (reference)
What the simulator uses at the moment (NOT from the DCS): to compare with the values you write.
Type | Station | MNO | Tag | Sheet | PH | PL | MH | ML | P (= 100 / Kp) | I (s) | D (s)
PID | 101 | 6 | PIC-COBM | ABC-001C | 150 | 0 | 100 | 0 | 100 | 60 | 0
PID | 101 | 9 | TICMS1004 | ABC-012 |  |  | 100 | 0 | 100 | 180 | 0
PID | 101 | 10 | AICFG112 | ABC-002 | 25 | 0 | 100 | 0 | 125 | 240 | 0
PID | 101 | 14 | FIC-CF | ABC-004A | 100 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 15 | FIC-CM | ABC-004A | 120 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 16 | TICBR1130 | ABC-011 | 600 | 0 | 100 | 0 | 100 | 180 | 0
PID | 101 | 17 | TICBR1140 | ABC-011 | 600 | 0 | 100 | 0 | 100 | 180 | 0
PID | 101 | 18 | TICBR1150 | ABC-012 | 600 | 0 | 100 | 0 | 100 | 180 | 0
PID | 101 | 19 | PICDO1008 | ABC-029 | 25 | 0 | 100 | 0 | 100 | 60 | 0
PID | 101 | 20 | LICBR1001 | ABC-010 | 820 | -422 | 100 | 0 | 100 | 120 | 0
PID | 101 | 21 | LICBR1001A | ABC-010 | 820 | -422 | 100 | 0 | 100 | 120 | 0
PID | 101 | 22 | FICFW1007 | ABC-010 | 550 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 23 | FICFA1071 | ABC-007 | 648 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 24 | FICFA1081 | ABC-007 | 432 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 25 | FICFA1055A | ABC-014 | 35 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 26 | FICFA1055B | ABC-014 | 35 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 27 | FICFA1043A | ABC-003A | 65 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 28 | FICFA1043B | ABC-003B | 65 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 29 | PICFG108A | ABC-008 | 600 | -600 | 100 | 0 | 100 | 60 | 0
PID | 101 | 30 | PICMS1002 | ABC-013 | 150 | 0 | 100 | 0 | 100 | 60 | 0
PID | 101 | 31 | DPICFG108 | ABC-009A | 2500 | 0 | 100 | 0 | 100 | 60 | 0
PID | 101 | 32 | PIC-BASC | ABC-009A | 100 | 0 | 100 | 0 | 100 | 60 | 0
PID | 101 | 33 | FICDO1043A | ABC-003A | 3.5 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 34 | FICDO1043B | ABC-003B | 3.5 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 35 | FICDO1043C | ABC-003C | 3.5 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 36 | PICFG108 | ABC-008 | 600 | -600 | 100 | 0 | 100 | 60 | 0
PID | 101 | 37 | AICFG10571 | ABC-005 | 500 | 0 | 100 | 0 | 125 | 240 | 0
PID | 101 | 38 | FICDO1043D | ABC-003D | 3.5 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 46 | PICHR1391 | ABC-054 | 50 | 0 | 100 | 0 | 100 | 60 | 0
PID | 101 | 49 | LICBR1001B | ABC-010 | 820 | -422 | 100 | 0 | 100 | 120 | 0
PID | 101 | 51 | HS-COAL | ABC-004A |  |  | 100 | 0 | 100 | 60 | 0
PID | 101 | 62 | PICDO1043A | ABC-003A |  |  | 100 | 0 | 100 | 60 | 0
PID | 101 | 63 | PICDO1043B | ABC-003B |  |  | 100 | 0 | 100 | 60 | 0
PID | 101 | 64 | PICDO1043C | ABC-003C |  |  | 100 | 0 | 100 | 60 | 0
PID | 101 | 65 | PICDO1043D | ABC-003D |  |  | 100 | 0 | 100 | 60 | 0
PID | 101 | 71 | HICBR1391 | ABC-055 | 100 | 0 | 100 | 0 | 100 | 60 | 0
PID | 101 | 164 | FIC-OM | ABC-003E |  |  | 100 | 0 | 100 | 15 | 0
PID | 101 | 197 | FICFA1043C | ABC-003C | 65 | 0 | 100 | 0 | 100 | 15 | 0
PID | 101 | 198 | FICFA1043D | ABC-003D | 65 | 0 | 100 | 0 | 100 | 15 | 0
PID | 102 | 1 | PICSB1052 | ABC-017 | 50 | 0 | 100 | 0 | 100 | 60 | 0
PID | 102 | 2 | PICMS1006 | ABC-050 | 150 | 0 | 100 | 0 | 100 | 60 | 0
PID | 102 | 3 | TICMS1022 | ABC-051 | 600 | 0 | 100 | 0 | 100 | 180 | 0
PID | 102 | 4 | LICCD1104 | ABC-031 | 1095 | -2335 | 100 | 0 | 100 | 120 | 0
PID | 102 | 5 | TICHR1002 | ABC-019 | 600 | 0 | 100 | 0 | 100 | 180 | 0
PID | 102 | 6 | TICHR1002A | ABC-020 | 600 | 0 | 100 | 0 | 100 | 180 | 0
PID | 102 | 7 | PICAS1004 | ABC-030 | 15 | 0 | 100 | 0 | 100 | 60 | 0
PID | 102 | 8 | PICAS1005 | ABC-030 | 15 | 0 | 100 | 0 | 100 | 60 | 0
PID | 102 | 9 | PICCD1104 | ABC-056 | 10 | 0 | 100 | 0 | 100 | 60 | 0
PID | 102 | 10 | LICCD1110A | ABC-031 | 464 | -436 | 100 | 0 | 100 | 120 | 0
PID | 102 | 11 | LICCD1110B | ABC-031 | 464 | -436 | 100 | 0 | 100 | 120 | 0
PID | 102 | 12 | FICCD1120 | ABC-032 | 400 | 0 | 100 | 0 | 100 | 15 | 0
PID | 102 | 13 | FICCD1121 | ABC-032 | 200 | 0 | 100 | 0 | 100 | 15 | 0
PID | 102 | 14 | TICAS1001 | ABC-033 | 600 | 0 | 100 | 0 | 100 | 180 | 0
PID | 102 | 15 | TICAS1017 | ABC-034 | 300 | 0 | 100 | 0 | 100 | 180 | 0
PID | 102 | 16 | LICHD11051 | ABC-035 | 310 | -300 | 100 | 0 | 100 | 120 | 0
PID | 102 | 17 | LICHD11052 | ABC-035 | 310 | -300 | 100 | 0 | 100 | 120 | 0
PID | 102 | 18 | LICHD11061 | ABC-036 | 310 | -300 | 100 | 0 | 100 | 120 | 0
PID | 102 | 19 | LICHD11062 | ABC-036 | 310 | -300 | 100 | 0 | 100 | 120 | 0
PID | 102 | 20 | LICHD11011 | ABC-037 | 290 | -320 | 100 | 0 | 100 | 120 | 0
PID | 102 | 21 | LICHD11012 | ABC-037 | 290 | -320 | 100 | 0 | 100 | 120 | 0
PID | 102 | 22 | LICHD11021 | ABC-038 | 295 | -315 | 100 | 0 | 100 | 120 | 0
PID | 102 | 23 | LICHD11022 | ABC-038 | 295 | -315 | 100 | 0 | 100 | 120 | 0
PID | 102 | 24 | LICHD11031 | ABC-039 | 300 | -310 | 100 | 0 | 100 | 120 | 0
PID | 102 | 25 | LICHD11032 | ABC-039 | 300 | -310 | 100 | 0 | 100 | 120 | 0
PID | 102 | 26 | PICHR1003 | ABC-052 | 50 | 0 | 100 | 0 | 100 | 60 | 0
PID | 102 | 27 | TICHR1012 | ABC-052 | 300 | 0 | 100 | 0 | 100 | 180 | 0
PID | 102 | 28 | TICLO1002 | ABC-053 | 100 | 0 | 100 | 0 | 100 | 180 | 0
PID | 105 | 1 | PICDO0005 | ABC-028 | 25 | 0 | 100 | 0 | 100 | 60 | 0
MAN | 101 | 2 | HIC-ULD | ABC-001A | 200 | 0
MAN | 101 | 3 | HIC-MWHL | ABC-001A | 200 | 0
MAN | 101 | 4 | HIC-MWLL | ABC-001A | 200 | 0
MAN | 101 | 5 | HIC-MWRL | ABC-001B | 10 | 0
MAN | 101 | 7 | HIC-BM | ABC-001C | 100 | 0
MAN | 101 | 8 | EIC-TM | ABC-001C | 200 | 0
MAN | 101 | 11 | FICCL1061A | ABC-004A | 40 | 0
MAN | 101 | 12 | FICCL1061B | ABC-004B | 40 | 0
MAN | 101 | 13 | FICCL1061C | ABC-004C | 40 | 0
MAN | 101 | 39 | HICL1060A | ABC-009A | 25 | -25
MAN | 101 | 40 | HICL1060B | ABC-009A | 25 | -25
MAN | 101 | 41 | HICL1060C | ABC-009A | 25 | -25
MAN | 101 | 42 | HICL1060D | ABC-009B | 25 | -25
MAN | 101 | 43 | HS-OIL | ABC-002 | 12000 | 8000
MAN | 101 | 44 | HIC-AFAR | ABC-003A | 1.2 | 0.8
MAN | 101 | 45 | HIC-BFAR | ABC-003B | 1.2 | 0.8
MAN | 101 | 48 | HS-O2 | ABC-002 | 4 | -4
MAN | 101 | 50 | HIC-TADBS | ABC-002 | 30 | -30
MAN | 101 | 52 | A-BIAS | ABC-004A | 8 | -8
MAN | 101 | 53 | B-BIAS | ABC-004B | 8 | -8
MAN | 101 | 54 | C-BIAS | ABC-004C | 8 | -8
MAN | 101 | 55 | SICL1060A | ABC-009A | 5 | 0
MAN | 101 | 56 | SICL1060B | ABC-009A | 5 | 0
MAN | 101 | 57 | SICL1060C | ABC-009A | 5 | 0
MAN | 101 | 58 | SICL1060D | ABC-009B | 5 | 0
MAN | 101 | 59 | HIC-CFAR | ABC-003C | 1.2 | 0.8
MAN | 101 | 60 | HIC-DFAR | ABC-003D | 1.2 | 0.8
MAN | 101 | 61 | HICDO1012 | ABC-029 | 100 | 0
MAN | 101 | 158 | HIC-SADBSA | ABC-003A | 10 | -10
MAN | 101 | 159 | HIC-SADBSB | ABC-003B | 10 | -10
MAN | 101 | 160 | HIC-SADBSC | ABC-003C | 10 | -10
MAN | 101 | 161 | HIC-SADBSD | ABC-003D | 10 | -10
MAN | 102 | 31 | HICHR1002A | ABC-020 | 100 | 0
MAN | 102 | 32 | HICHR1002B | ABC-020 | 100 | 0
MAN | 103 | 1 | HICFA1005 | ABC-015 | 100 | 0
MAN | 103 | 2 | HICFA1006 | ABC-015 | 100 | 0
MAN | 103 | 3 | HICFA1007 | ABC-015 | 100 | 0
MAN | 103 | 4 | HICFA1008 | ABC-015 | 100 | 0
MAN | 103 | 5 | HICFA1009 | ABC-015 | 100 | 0
MAN | 103 | 6 | HICFA1010 | ABC-015 | 100 | 0
MAN | 103 | 7 | HICFA1011 | ABC-015 | 100 | 0
MAN | 103 | 8 | HICFA1012 | ABC-015 | 100 | 0
MAN | 103 | 9 | HICFA1013 | ABC-015 | 100 | 0
MAN | 103 | 10 | HICFA1014 | ABC-015 | 100 | 0
MAN | 103 | 11 | HICFA1015 | ABC-015 | 100 | 0
MAN | 103 | 12 | HICFA1016 | ABC-015 | 100 | 0
MAN | 103 | 13 | HICFA1017 | ABC-016 | 100 | 0
MAN | 103 | 14 | HICFA1018 | ABC-016 | 100 | 0
MAN | 103 | 15 | HICFA1019 | ABC-016 | 100 | 0
MAN | 103 | 16 | HICFA1020 | ABC-016 | 100 | 0
MAN | 103 | 17 | HICFA1021 | ABC-016 | 100 | 0
MAN | 103 | 18 | HICFA1022 | ABC-016 | 100 | 0
MAN | 103 | 19 | HICFA1023 | ABC-016 | 100 | 0
MAN | 103 | 20 | HICFA1024 | ABC-016 | 100 | 0
MAN | 103 | 21 | HICFA1025 | ABC-016 | 100 | 0
MAN | 103 | 22 | HICFA1026 | ABC-016 | 100 | 0
MAN | 103 | 23 | HICFABIASU | ABC-057 | 10 | -10
MAN | 103 | 24 | HICFABIASL | ABC-057 | 100 | 0